## Introduction
PNNL-SA-171971
Generator Runtime Analysis
This Excel-based Generator Runtime Analysis sheet is a tool to calculate how many days a generator can support its critical loads. This information is an input for characterizing redundant systems in the TRN risk assessment methodology as part of Baseline Development (BD) Action 3. This tool provides two different options for calculating runtime:
1. If daily consumption (kWh) is known or reliable estimate is available
2. If daily fuel consumption is unknown, but generator size is known
Using either of these options, the user will get an output establishing the number of days thatcurrent redundant systems will be able to meet critical loads. The user can directly input the results of this analysis for the “Estimated Run Time (hrs)” in BD Action 3 for the redundant system being analyzed. This analysis provides a high-level estimate. For users who have done or are planning to do more refined assessments of the runtime capabilities for their redundant systems, those estimates may be more appropriate to use as inputs for the TRN analysis. This tool provides estimates for runtime only for generators operating using fossil fuels. For other types of electric redundant systems, the user should use other resources to characterize their runtime capabilities.
This format denotes data entry cells.
This format denotes cells that should not be edited.
This format denotes cells that are final values.
Required User Inputs
1. Fuel type (Diesel, Propane, Gasoline, LNG, or Fuel Oil)*
2. Estimated daily consumption (kWh) OR generator size (kW)
3. Generator daily load factor % (Option 2 only)
4. Assumed generator efficiency %
5. Onsite fuel storage capacity (gal)
6. Refueling information if applicable
*Natural gas is not included as a fuel type for generators in this tool. Natural gas generators are connected directly to a natural gas line. Unless a natural gas disruption has also occurred, a natural gas generator will have an "infinite" runtime. However, natural gas generator manufacturers recommend running for no longer than 500 hours at a time so the generator can cool down and any required oil changes or filter replacements can be conducted.

## Generator Fuel Analysis
Generator Fuel Use Analysis
Use this worksheet to establish the number of days current redundant systems will be able to meet critical loads. The results will be used in Baseline Development Action 3.
This format denotes data entry cells.
This format denotes cells that should not be edited.
This format denotes cells that contain final values.
Option 1 | If daily consumption (kWh) is known or reliable estimate is available:
| Step | Description | Data Entry & Calculations | Comment
| 1 | Fuel type | Diesel | Select fuel type from dropdown list
| 2 | Estimated daily consumption (kWh)* | 2400 | Include consumption from all loads (whether critical or not) supported by the generator
| 3 | Assumed generator efficiency | 30% | For a diesel generator, 30% is a typical efficiency; older and part-loaded equipment will be 20-25%, and new or larger generators can be up to 40% efficiency. For other fuel types, the efficiency may be similar, but check the generator manufacturer website for a closer estimate.
| 4 | kWh to BTU conversion | 3412 | BTU per kWh
| 5 | Daily fuel consumed by generator (BTUs) | 27296000 | Daily consumption X BTUs per kWh / Generator efficiency
| 6 | BTU content of fuel per gallon | 137381 | Diesel, propane, gasoline, fuel oil: https://www.eia.gov/energyexplained/units-and-calculators/ LNG: https://www.extension.iastate.edu/agdm/wholefarm/html/c6-89.html
| 7 | Gallons per day consumed | 198.6883 | Daily fuel input / BTU content of fuel
| 8 | Onsite fuel storage capacity (gal) | 1000 | Only include fuel that would be allocated to this generator
| 9 | Days critical load can be met | 5.033
| 10 | If available, can offsite fuel delivery arrive prior to end of period calculated in step 9 (5.0 days)? | Yes | Additional fuel may be obtained via contracted delivery, mutual aid agreement, etc.
| 11 | If refueled, will the fuel storage dedicated to the generator be completely refueled? | No | These calculations assume that refueling occurs with 20% fuel remaining
| 12 | If answered "No" in step 11, how many gallons will be supplied? | 500 | Only include fuel that would be allocated to this generator
| 13 | Additional days provided by a single refueling | 2.5165 | These calculations assume that refueling occurs with 20% fuel remaining
| 14 | Is the refueling availability recurring or a one-time event? | One-time | If recurring, must arrive again within 2.5 days since last delivery
| 15 | Longest duration of outage this redundant system could support (days) | 7.5495
| 16 | Longest duration of outage this redundant system could support (hours) | 181 | This number will be entered into Baseline Development Action 3
* Assumed that generator has sufficient capacity to meet required kW demand
Option 2 | If daily fuel consumption is unknown, but generator size is known:
| Step | Description | Data Entry & Calculations | Comment
| 1 | Fuel type | Diesel | Select fuel type from dropdown list
| 2 | Generator size (kW) | 500 | Include capacity dedicated to all loads (whether critical or not) supported by the generator
| 3 | Generator daily load factor (%) | 25% | % of total generator output used to serve load over the course of the day (e.g., 100kW generator could produce 2400kWh in a day, but in practice may only produce 600kWh)
| 4 | Assumed generator efficiency | 30% | For a diesel generator, 30% is a typical efficiency; older and part-loaded equipment will be 20-25%, and new or larger generators can be up to 40% efficiency. For other fuel types, the efficiency may be similar, but check the generator manufacturer website for a closer estimate.
| 5 | kWh to BTU conversion | 3412 | BTU per kWh
| 6 | Daily fuel consumed by generator (BTUs) | 34120000 | Generator size X Daily load factor X 24 hrs X BTUs per kWh / Generator efficiency
| 7 | BTU content of fuel per gallon | 137381 | Diesel, propane, gasoline, fuel oil: https://www.eia.gov/energyexplained/units-and-calculators/ LNG: https://www.extension.iastate.edu/agdm/wholefarm/html/c6-89.html
| 8 | Gallons per day consumed | 248.3604 | Daily fuel input / BTU content of fuel
| 9 | Onsite fuel storage capacity (gal) | 800 | Only include fuel that would be allocated to this generator
| 10 | Days critical load can be met | 3.2211
| 11 | If available, can offsite fuel delivery arrive prior to end of period calculated in step 10 (3.2 days)? | Yes | Additional fuel may be obtained via contracted delivery, mutual aid agreement, etc.
| 12 | If refueled, will the fuel storage dedicated to the generator be completely refueled? | No | These calculations assume that refueling occurs with 20% fuel remaining
| 13 | If answered "No" in step 12, how many gallons will be supplied? | 500 | Only include fuel that would be allocated to this generator
| 14 | Additional days provided by a single refueling | 2.0132 | These calculations assume that refueling occurs with 20% fuel remaining
| 15 | Is the refueling availability recurring or a one-time event? | Recurring | If recurring, must arrive again within 2.0 days since last delivery
| 16 | Longest duration of outage this redundant system could support (days) | 6 months or more
| 17 | Longest duration of outage this redundant system could support (hours) | 4500 | This number will be entered into Baseline Development Action 3

## Fuel Dropdown (hidden)
Fuel Type | BTU Content
Diesel | 137381
Propane | 91452
Gasoline | 120286
LNG | 69514
Fuel Oil | 149690